SPECIFICATION FOR

SMITH & LOVELESS FLOODED SUCTION

IMMERSIBLE NON-CLOG PUMPS

GENERAL

The contractor shall furnish and install _____________ vertical, close-coupled, motor-driven, IMMERSIBLE, non-clog type pumps as manufactured by Smith & Loveless, Inc., Lenexa, Kansas.

OPERATING CONDITIONS

Each pump shall be capable of delivering 	 GPM of raw water or wastewater against a total dynamic head of

feet.  The minimum acceptable pump efficiency at this condition shall be 	%.  Due to the energy conservation requirements, the minimum efficiency will be enforced.  The maximum allowable speed shall be 	 RPM.  The minimum rated horsepower of each pump motor shall be 	.

All openings and passages shall be large enough to permit the passage of a sphere three inches (3”) in diameter.  The anticipated operating head range is from 	 feet minimum to 	 feet maximum.

PUMPS

The pumps shall be 	 inches vertical, non-clog type of heavy cast-iron construction, especially designed for the use of mechanical seals.  In order to minimize seal wear caused by linear movement of the shaft, the shaft bearing nearest the pump impeller shall be locked in place so that end play is limited to the clearance within the bearing.  To minimize seal wear resulting from shaft deflection caused by the radial thrust of the pump, the shaft from the top of the impeller to the lower bearing supporting the impeller shall have a minimum diameter of 1-7/8” for motor frame sizes 213 through 286; 2-1/8” for motor frame sizes 324 and 326; and 3” for frame 364 and larger.  The dimension from the lowest bearing to the top of the impeller shall not exceed six inches (6”).

The bearing nearest the impeller shall be designed for the combined thrust and radial load.  The upper bearing shall be free to move linearly with the thermal expansion of the shaft, and shall carry only radial loads.

The shaft shall be solid stainless steel through the mechanical seal to eliminate corrosion and abrasive rust particles.  Removable shaft sleeves will not be acceptable if the shaft under the sleeve does not meet the specified minimum diameter.

[note to designer: select one of the following pump type paragraphs, a or b, and delete the other.  check pump curves for proper application]

A.  non-clog two-port impeller

The pump impeller shall be of the enclosed two-port type made of close-grained cast iron, and shall be balanced.  The eye of the impeller, as well as the ports, shall be large enough to permit the passage of a sphere three-inches (3”) in diameter, in accordance with nationally recognized codes.  The impeller shall be keyed with a stainless steel key and secured to the motor shaft by a stainless steel capscrew equipped with a Nylock or other suitable self-locking device.  The impeller shall not be screwed or pinned to the motor pump shaft, and shall be readily removable without the use of special tools.  To prevent the buildup of stringy materials, grit and other foreign particles around the pump shaft, all impellers less than full diameter shall be trimmed inside the impeller shrouds.  The shrouds shall remain full diameter so that close minimum clearance from shrouds to volute is maintained.  Both the end of the shaft and the bore of the impeller shall be tapered to permit easy removal of the impeller from the shaft.

B.  X-PELLER SUPER CLOG-RESISTANT MONO-PORT IMPELLER (4” & 6” OPTION)

The pump impeller shall be of the enclosed mono-port type made of close-grained cast iron, and shall be in dynamic balance when pumping wastewater.  Two (2) port impellers are specifically disallowed.  The dynamic balance shall be obtained without the use of balance weights or liquid-filled chambers.  The impeller shall be designed to allow for the trimming of the impeller to meet design condition changes without altering the balance.  The eye of the impeller, as well as the port, shall be large enough to permit the passage of a sphere three inches (3”) in diameter, in accordance with nationally recognized codes.  To further prevent clogging, the impeller port shall have a minimum area 10.6 in2.  The impeller shall be keyed with a stainless steel key and secured to the motor shaft by a stainless steel capscrew equipped with a Nylock or other suitable self-locking device.  The impeller shall not be screwed or pinned to the motor pump shaft, and shall be readily removable without the use of special tools.  To prevent the buildup of stringy materials, grit and other foreign particles around the pump shaft, all impellers less than full diameter shall be trimmed inside the impeller shrouds.  The shrouds shall remain full diameter so that close minimum clearance from shrouds to volute is maintained.  Both the end of the shaft and the bore of the impeller shall be tapered to permit easy removal of the impeller from the shaft.

The motor shall be attached to the pump volute by a one-piece cast iron adapter and backhead.  The pump shall be arranged so that the rotating element may easily be removed from the volute without disconnecting the seal system or electrical wiring.  The pump shall be arranged so that any foreign object may be removed from the pump or suction elbow without disassembling the motor, impeller or backhead.  Volute or suction elbow clean-outs will not be an acceptable substitute.

The pump shaft shall be sealed against leakage by a double mechanical seal installed in a bronze seal housing constructed in two (2) sections with registered fit.  The housing shall be recessed into the pump backhead and securely fastened thereto with stainless steel capscrews.  The inside of the seal housing shall be tapered to facilitate the replacement of the seal parts. The seal shall be a double seal, with the mating surfaces lapped to a flatness tolerance of one light band.  The rotating member shall be held in mating position with the stationary carbons by a stainless steel spring.  The seal housing with assembled parts shall be so constructed as to be readily removable from the shaft as a unit, and shall be provided with tapped jackscrew openings to assist in removing it from the backhead.

The seal shall be pressurized and lubricated by water taken directly from the pump backhead.  The water shall pass through a filter to the seal housing and be introduced between the upper and lower sealing surfaces.  The filter shall be of corrosion-resistant materials, and shall screen out all solids larger than 50 microns.  The seal system shall contain a brass valve connected near the top of the seal housing to permit the relief of any air trapped in the seal unit.  A manually operated brass valve shall also be provided to vent the pump volute.

The pump volute shall be of heavy, cast iron construction, free from projections that might cause clogging or interfere with flow through the pump.  The volute casing shall be (dual-curved) (double-volute) to reduce radial thrust.

The pump shall be supported by a heavy base with four (4) legs to provide maximum rigidity and balance.  The height shall be sufficient to permit the use of an increasing suction elbow, which shall be provided when the nominal pump size is smaller than the suction line.  The suction and discharge openings shall be flanged, faced and drilled 125-pound American Standard.

MOTORS

The pump motors shall be vertical, solid shaft, NEMA P-base, squirrel-cage induction type, suitable for 	 phase, 	 cycle, 	 volt electric current.  They shall have Class F insulation.  The insulation temperature shall, however, be limited to Class B.  The motors shall have normal starting torque and low-starting current, as specified by NEMA Design B characteristics.

The motors shall be immersible for up to three (3) weeks at a depth of thirty feet (30’) of water without damage from leakage.  After returning from an immersed state, the motor shall be capable of being restarted without any service to the motor.  If the motor is operated in the immersed state, minor on-site repairs, consisting of replacing the cooling fan may have to be made prior to normal operation in air.  The upper and lower shaft extensions shall be sealed with specially designed PTFE rotating lip seals and all casting-to-casting interfaces shall be sealed with Viton O-rings.  Leads shall be terminated in a cast connection box, designed to exclude moisture, and all leads shall be clearly identified.  Where required for sealing, all bolts shall be provided with Neoprene-backed washers.  In addition, a slinger ring shall be provided on the lower shaft extension to further reduce the possibility of water entering the motor.

Each motor shall have at least one (1) normally closed, automatically resetting thermostat per phase, suitable for a 120 VAC 2-amp load.

MOTOR OPTIONS [DESIGNER: SELECT IF REQUIRED]

 	Space Heater: A 120 VAC space heater shall be provided in the motor enclosure to combat condensation.  Leads shall be brought out through the conduit box.

	Moisture Sensor: A moisture detector shall be provided at the low spot in the motor housing to sense the presence of liquid and close alarm contacts.  Leads shall be brought out through the conduit box.

The motors shall have 1.15 service factor.  The service factor shall be reserved for the owner’s protection.  The motors shall not be overloaded beyond their nameplate rating, at the design condition, or at any head in the operating range as specified under Operating Conditions.

The motor-pump shaft shall be centered, in relation to the motor base, within .005”.  The shaft run-out shall be limited to .003”.

The motor shaft shall equal or exceed the diameter specified under “pumps”, at all points from immediately below the top bearing to the top of the impeller hub.

A bearing cap shall be provided to hold the bottom motor bearing in a fixed position.  Bearing housings shall be provided with plugged fittings for lubrication, as well as purging old lubricant.

The motors shall be fitted with heavy lifting eyes or lugs, each capable of supporting the entire weight of the pump and motor.

SPARE PARTS

The manufacturer of the pump shall furnish a complete replacement pump shaft seal assembly, packaged in a suitable container with complete installation instructions.

A spare filter element for the seal filter shall be provided.

A spare volute gasket shall be provided.

A spare cooling fan shall be provided.

WARRANTY

The manufacturer of the pumps shall warranty for one (1) year from the date of shipment that the pumps will be free from defects in design, material and workmanship.

Warranties by the suppliers of various components in lieu of a single source responsibility by the manufacturer will not be accepted.  The manufacturer shall assume prime responsibility for the warranty of the complete pump-motor units.

In the event a component fails to perform as specified, or is proven defective in service during the warranty period, the manufacturer shall repair or replace, at his discretion, such defective part.

The replacement or repair of those items normally consumed in service such as seals, grease, etc., shall be considered as part of routine maintenance and upkeep.

It is not intended that the manufacturer of the pumps assume responsibility for contingent liabilities or consequential damages of any nature resulting from defects in design, material, workmanship or delays in delivery, replacement or otherwise.

MANUFACTURER’S INSURANCE

ALL EQUIPMENT MANUFACTURERS, either direct or subcontractors to the general or mechanical contractors, SHALL HAVE in effect at TIME OF BID, CONTRACT AWARD, CONTRACT PERFORMANCE, and WARRANTY TERM, PRODUCT AND COMPREHENSIVE LIABILITY INSURANCE, INCLUDING SUDDEN AND ACCIDENTAL POLLUTION COVERAGE in the amount of FIVE MILLION DOLLARS, $5,000,000, through an insurance company with a minimum rating of A+ (SUPERIOR) XV according to the BEST’S INSURANCE REPORTS. All policies must be written on an OCCURRENCE BASIS. Policies written on a CLAIMS MADE BASIS are not acceptable.  A typical CERTIFICATE OF INSURANCE attesting to the specified coverage issued by the responsible carrier naming the ENGINEER OF RECORD and the OWNER as ADDITIONAL INSURED must be presented to the named additional insured prior to contract award. A FAILURE TO COMPLY with this requirement BY THE BIDDER will require DISQUALIFICATION of the BID and CONTRACT AWARD.

MANUFACTURED EQUIPMENT

Option 1 (Standardization) [delete this line from final spec text]

The specifications and drawings detail Smith & Loveless equipment and represent the minimum standard of quality for both equipment and materials of construction.  The contractor shall prepare his bid on the basis of the particular equipment and materials specified for the purpose of determining the low bid.

The owner has standardized on the named equipment in order to optimize their operation, facilitate maintenance and safety programs, provide for interchangeability of costly equipment items, reduce stocking levels required for necessary spare parts and provide increased flexibility in the utilization of their treatment equipment.  Equipment substitutions, since incompatible with the district's standardizations program, will not be considered.

Option 2 (Base Bid with Bid Submittal) [delete this line from final spec]

The specifications and drawings detail Smith & Loveless equipment and represent the minimum standard of quality for both equipment and materials of construction.  The contractor shall prepare his bid on the basis of this equipment for the purpose of determining the low bid without consideration of a possible substitute.  Substitution of other makes may be considered if the equipment proposed for substitution is superior or equal in quality and efficiency to the standards of quality named in the specifications and this is demonstrated to the satisfaction of the engineer.  Contractors wishing to offer a deduct for substitute equipment shall include the following submittal information with their proposal.

Bid Submittal

This submittal shall include all necessary information for the proper determination of the acceptability of the proposed substitution and shall not necessarily be limited to the following.

- Complete description of the equipment, system, process, or function, including a list of system components and features, drawings, catalog information and cuts, manufacturer's specifications, including materials description.

- Performance data and curves, and horsepower requirements.

- Outside utility requirements, such as water power, air, etc.

- Functional description of any internal instrumentation and control supplied including list of parameters monitored, controlled, or alarmed.

- Addresses and phone numbers of nearest service centers and a listing of the manufacturer's or manufacturer's representatives' services available at these locations, including addresses and phone numbers of the nearest parts warehouses capable of providing full parts replacement and/or repair services.

- A list of five installations in the states where similar equipment by the manufacturer is currently in similar service; include contact name, telephone number, mailing address of the municipality or installation, engineer, owner, and installation contractor; if five installations do not exist, the list shall include all that do exist, if any.

- Detailed information on site, architectural, structural, mechanical, plumbing, electrical, and control, and all other changes or modifications to the design and construction work necessary to adapt the equipment or systems to the arrangement shown and/or functions described on the drawings and in the technical specifications.  This shall include plan view and section sketches illustrating any additional space requirements necessary to provide the minimum adequate clear space within and around the equipment for operation and maintenance, as shown on the drawings and specified.

- All differences between the specifications and the proposed substitute equipment shall be clearly stated in writing under a heading of "differences".

- Other specified submittal requirements listed in the detailed equipment and material specifications.

- A completed and signed copy of the “Flooded Suction Rotating Assembly Certification Affidavit” which follows.

Evaluation

Approval of the substitution to bid as an alternate shall in no way relieve the contractor from submitting the specified shop drawings for approval or complying fully with all provisions of the specifications and drawings.

If substituted equipment is accepted, the contractor shall, at his own expense, make any changes in the structures, piping, electrical, etc. necessary to accommodate the equipment.  If engineering is required due to substitution of alternate equipment, the contractor shall pay for all engineering charges.

To receive final consideration, copies of the manufacturers' quotations for the equipment may be required to document the savings to the satisfaction of the engineer.  It is the intent that the owner shall receive the full benefit of the savings in cost of equipment and the contractor's bid price shall be reduced by an amount equal to the savings.  In all technical and other evaluations, the decision of the engineer is final.

TYPICAL BID FORM

(add to bid form as applicable to above selected option]

OPTION 1

For reasons of standardization, bids shall be based on the named equipment. Alternate bids will not be allowed.

OPTION 2

The bid shall be based on the named equipment. Alternate/substitute equipment may be offered as a deduct, provided all conditions of the “manufactured equipment” section are met.

Alternate/substitute manufacturer				.

Deduct $				.

# Flooded NON-CLOG PUMP assembly CERTIFICATION AFFIDAVIT

A submittal will be required to be submitted to the owner by manufacturers proposing alternate, unnamed pumps with their bid.  Included in the submittal shall be full-size drawings and detailed specifications on the proposed pump.  Copies of the engineer’s plans and specifications will not be acceptable.  Included in the bid submittal shall be the following filled-out checklist. It shall be signed by an officer of the Company.

|  | YES | NO |
| --- | --- | --- |
| Close-coupled pump design - no motor to pump shaft coupling |  |  |
| Pump shaft diameter of minimum through seal |  |  |
| Full diameter impeller shrouds |  |  |
| Stainless steel pump shaft |  |  |
| Tapered shaft to impeller fit |  |  |
| Maximum pump shaft overhang of 6”- lower bearing to impeller |  |  |
| Bronze seal housing |  |  |
| Minimum pump efficiency at design point of GPM of % |  |  |
| % pump efficiency at best efficiency point for proposed impeller |  |  |
| Class F motor insulation with Class B max motor temperature rise and 1.15 service factor |  |  |
| Motor shaft run-out 0.003” max |  |  |
| Motor shaft centered to motor base with 0.005” |  |  |
| Locked lower bearing and floating upper bearing |  |  |
| One-piece motor adapter/backhead |  |  |
| Motor HP of at RPM |  |  |
| Double mechanical seal with rotating ceramic elements and stationary carbon elements |  |  |
| 50 micron seal water filters |  |  |
| Seal water taken from low pressure area of pump backhead |  |  |
| Product liability insurance, $5 million per specification |  |  |

The consulting engineer shall be the sole judge of whether the proposed equipment is acceptable. The manufacturer shall have the responsibility of submitting sufficient information in one submission. Incomplete or inaccurate submittal data shall be cause for rejection of the proposed equipment.

By an officer of the company signing this affidavit, he has stated 100% compliance with the plans and specifications and further states he will supply or pay for all deficiencies found in the job submittals or after the unit is installed. The consulting engineer shall be the sole judge regarding compliance with the plans and specifications and shall be sole judge on the amount of moneys required if any deficiencies are found. Generally, the amount of money shall be related to, but not limited to, a 20-year pump design life.

Signature of Company Officer

Corporate Seal

(Notarized)									    Title